## Slide 1: Evaluation des débits d’eaux claires dans un réseau unitaire à partir d’enregistrements de turbidité et de conductivité
M. Aumond, C. Joannis
L.C.P.C
GEMCEA
Notes: I am claude Joannis, my co-author is Michel Aumond, and we both work at the central laboratory of civil engineering in France
Our presentation is about assessing infiltration and inflow discharges from turbidity and conductivity measurements.
You will see in the presentation that we are focusing on dry weather conditions, so that the infiltration component of infiltration and inflow is the main concern

## Slide 2: Données
BV Duchesse Anne (Nantes):
25 km2, 150 000 e.h.
20 000 – 60 000 m3/j
mixte unitaire + separatif
Acquisition à 5 mn
(2 turbi redondants +filtrage)
Analyse à une heure
Une année ~ 180 jours secs
turbidité (FAU)
conductivité (S/cm)
débit (m3/s)
Notes: The data processed for this presentation were recorded over a period of one year, with a time-step of 5 minutes, at the outlet of a large catchment in the city of Nantes. This is serviced by a combined system at the downstream part, and a separate system at the upstream part of the catchment.
Here is a sample of recordings for a few days in june. Flowrate is black, turbidity is red and conductivity is blue.
We can spot similat dry weather patterns on all three parameters, may be more contrasted for turbidity.
During rain events flowrates increase sharply, whereas conductivity and even turbidity drop, which is clue for dilution effects. These dilution effects are easily seen immediately after rain events, but they occur all the year round with different time scales.
What we want is using this dilution effect to assess infiltration flowrates.

## Slide 3: 2 modèles de dilution
Q.C = (Q-Qi).Cs + Qi Ci
2 équations 2 (1) inconnues 3 variables mesurées
Notes: From the general equation for mass conservation of any conservative parameter, we can derive 2 equations giving infiltration flow-rate as an expression of total flow-rate and turbidity or conductivity.
The two equations are is a bit different because the turbidity of infiltration water is assumed to be zero which is not the case for conductivity.
Of course we would like that the two values for infiltration flow-rates are consistent, that is nearly equal.

## Slide 4: 2 modèles de dilution
Q.C = (Q-Qi).Cs + Qi Ci
2 équations 2 (1) inconnues 3 paramètres
Notes: Unfortunately, or maybe fortunately, we have got three parameters to asses before deriving Infiltration discharge. These are sanitary water conducivity and turbidity, and infiltration water conductivity.
We expect that these parameters can be calibrated so that values of infiltration flow-rates derived from both equations are consistent.

## Slide 5: 3 hypothèses
H 1: pour les eaux usées non diluées, seul le débit varie en fonction de l’heure de la journée. Toutes les concentrations restent constantes
H 2: pour les infiltrations, toutes les concentrations restent constantes
H 3: les variations des débits d’infiltration sont négligeables à l’échelle de la journée
Hypothèses = référence
Notes: But we must make some further assumptions.
The equations are verified for any time step, and the values of the parameters may be different for each time step.
To simplify and somewhat constraint the problem, we assumed that concentrationS of sanitary water are constant , as well as the conductivity of infiltration water. We also assumed that infiltration flow-rate was constant at the time-scale of one day.
We do know that these assumtions are very crude and indeed some of them we relaxed in a further step. But we feel that the can provide a useful reference, and analysing the discrepancies from these assumptions should be interesting.
Anyway our first attempts to assess parameter values provided very different results for Iinfiltration discharges derived either from conductivity or from turbidity. So we tried to get more consistenct results

## Slide 6
Débit (m3/s)
Conductivité de l’eau d’infiltration
(pente)
conductivité de l’eau usée
(pente)
Flux de conductivité
(S.m3/m.s)
.
Infiltration
eau usée
Infiltration
Eau
usée
turbidité de l’eau usée
(pente)
Flux de turbidité
FAU.m3/S.
eau usée
Graphe flux-débit
Notes: For checking the assumptions and calibrating the parameters we used a graphical analysis tool, which is a mass discharge vs. Flow-rate chart.
This chart represents flow rates as ordinates, and mass-discharges as abscissae. Turbidity data are red and conductivity data are blue . So in our case the mass discharges are rather unconventional, as they rely on conductivity and turbidity rather than on real concentrations, hence some strange units like
Anyway the assumptions of the dilution model, that are constant concentrations for sanitary water and infiltration water should lead to clouds of dots with the shape of parallelograms, with the gradient of the sides respectively equal to turbidty and conductivity values of sanitary water and infiltration water. Moroever the path of data observed for different dry days should be parrallel segments.
One interesting thing is that we get two consctructions for assessing infiltration flow rate and of course they should converge on the same point.

## Slide 7
FQ vs. MV
MV: flux et débits cumulés et normalisés
pour un paramètre (MES)
par événement pluvial
FQ: flux et débits non cumulés et non normalisés
pour deux paramètres
pour des données continues
( analyse / journée des données de temps sec)
tQ/V
T
C
Q
t/M
Notes: For checking the assumptions and calibrating the parameters we used a graphical analysis tool, which is a mass discharge vs. Flow-rate chart.
This chart represents flow rates as ordinates, and mass-discharges as abscissae. Turbidity data are red and conductivity data are blue . So in our case the mass discharges are rather unconventional, as they rely on conductivity and turbidity rather than on real concentrations, hence some strange units like
Anyway the assumptions of the dilution model, that are constant concentrations for sanitary water and infiltration water should lead to clouds of dots with the shape of parallelograms, with the gradient of the sides respectively equal to turbidty and conductivity values of sanitary water and infiltration water. Moroever the path of data observed for different dry days should be parrallel segments.
One interesting thing is that we get two consctructions for assessing infiltration flow rate and of course they should converge on the same point.

## Slide 8
débit (m3/s)
Flux de conductivité
S/cm x m3/s
Flux de turbidité
FAU x m3/s.
750 500 250 0 250 500 750
1
0,5
0
Graphe flux-débit: résultats
Notes: So let us have a look at real data. Dots represent every hourly recording in the measuring period, both with dry weather condition or rain events.

## Slide 9
750 500 250 0 250 500 750
1
0,5
0
débit (m3/s)
Flux de conductivité
S/cm x m3/s
Flux de turbidité
FAU x m3/s.
Graphe flux-débit: résultats
Notes: A proeminent feature is that mass discharges decrease when flow rate increases behond a threshold value, which is around 0.45 m3/S.
The decrease of mass discharge is quite obvious for conductivity, and less clear for turbidity. Overflow devices exist upstream from the measuring point and they might explain this behaviour,
if more concentrate wastewater from the separate system is overflowed, and more dilute wastewater is input downstream. But further anlysis and modelling are needed to check this explaination.

## Slide 10
750 500 250 0 250 500 750
1
0,5
0
débit (m3/s)
Flux de conductivité
S/cm x m3/s
Flux de turbidité
FAU x m3/s.
Graphe flux-débit: résultats
Notes: A proeminent feature is that mass discharges decrease when flow rate increases behond a threshold value, which is around 0.45 m3/S.
The decrease of mass discharge is quite obvious for conductivity, and less clear for turbidity. Overflow devices exist upstream from the measuring point and they might explain this behaviour,
if more concentrate wastewater from the separate system is overflowed, and more dilute wastewater is input downstream. But further anlysis and modelling are needed to check this explaination.

## Slide 11
750 500 250 0 250 500 750
1
0,5
0
débit (m3/s)
Flux de conductivité
S/cm x m3/s
Flux de turbidité
FAU x m3/s.
Graphe flux-débit: résultats
Pertes de flux > pertes de débit: DO /effluents concentrés
Notes: A proeminent feature is that mass discharges decrease when flow rate increases behond a threshold value, which is around 0.45 m3/S.
The decrease of mass discharge is quite obvious for conductivity, and less clear for turbidity. Overflow devices exist upstream from the measuring point and they might explain this behaviour,
if more concentrate wastewater from the separate system is overflowed, and more dilute wastewater is input downstream. But further anlysis and modelling are needed to check this explaination.

## Slide 12
750 500 250 0 250 500 750
1
0,5
0
débit (m3/s)
Flux de conductivité
S/cm x m3/s
Flux de turbidité
FAU x m3/s.
Graphe flux-débit: résultats
Débits écrêtés en bas de gamme
Notes: A proeminent feature is that mass discharges decrease when flow rate increases behond a threshold value, which is around 0.45 m3/S.
The decrease of mass discharge is quite obvious for conductivity, and less clear for turbidity. Overflow devices exist upstream from the measuring point and they might explain this behaviour,
if more concentrate wastewater from the separate system is overflowed, and more dilute wastewater is input downstream. But further anlysis and modelling are needed to check this explaination.

## Slide 13
Conductivity discharge
S/cm x m3/s
Turbidity discharge
FAU x m3/s.
750 500 250 0 250 500 750
1
0,5
0
Graphe flux-débit: résultats
débit (m3/s)
Flux de conductivité
S/cm x m3/s
Flux de turbidité
FAU x m3/s.
Un jour sec; un jour de pluie
Notes: So let us have a look at real data. Small dots represent every hourly recording in the measuring period, both with dry weather condition or rain events. Large dots are for a particular dry day. As expected the dots for a dry day are more or less aligned,
and we will analyse dry weather discharge a bit later
The plot is very different during a rain event, with higher flowrates and lower mass discharges than in dry weather conditions.
, at least for conductivity, lines are for a particular rainy day

## Slide 14
R>0.9: 80% jours secs pour conductivité 63% pour turbidité
500 250 0 250 500
1
0,5
0
0,1
0,2
0,3
0,4
débit (m3/s)
Flux de conductivité
S/cm x m3/s
Flux de turbidité
FAU x m3/s.
Graphe flux-débit: résultats
Notes: If we focus on a dry days not affected by these possible overflows, a linear fitting performs fairly well, especially for conductivity:. correlation coefficient over 0.9 are obtained for 80% of dry days for conductivity and 63% days for turbidity.
Indeed we have some doubt on the validity of linear fitting for turbidity, yet it provides some information on the mean value of genuine sanitary water

## Slide 15: Variations de paramètres et incertitudes
Conductivité (S/cm)
turbidité (FAU)
La concentration des EU strictes varie d’un jour à l’autre
Notes: If we plot all sanitary water conductivity and turbidity values fitted for dry days ,we can see a central zone, where the values for turbidity and conductivity are independant. The scattering is of the order of magnitude of the uncertainty of the fit. But we also see a larger range of variations, where both parametres are correlated, and which could be related to real variations of sanitary water daily mean concentration. Some common trends can be observed on the time diagram on right, but scattering remains very high.

## Slide 16
0.14 + 0.02 m3/s
0.22 + 0.05 m3/s
400 S/cm
0,1
0,2
0,3
0,4
Conductivity discharge
mS/m x m3/s
Turbidity discharge
FAU x m3/s.
500 250 0 250 500
1
0,5
0
0,1
0,2
0,3
0,4
Estimations divergentes des débits d’eaux d’infiltration à partir de la conductivité et de la turbidté
débit (m3/s)
Flux de conductivité
S/cm x m3/s
Flux de turbidité
FAU x m3/s.
Graphe flux-débit: résultats
Notes: I we try to assess infiltration discharge, a discrepancy appears between infiltration flow-rate values assessed either from conductivity or turbidity. This difference is quite general: it appears for 95 % of dry days. Its mean value is nearly 0.1 m3/s, which is really huge, although the conductivity of infiltration water is set to its upper limit of 400 mS/cm

## Slide 17
0,1
0,2
0,3
0,4
Conductivity discharge
mS/m x m3/s
Turbidity discharge
FAU x m3/s.
500 250 0 250 500
1
0,5
0
0,1
0,2
0,3
0,4
La turbidité des eaux usées strictes varie au cours de la journée
débit (m3/s)
Flux de conductivité
S/cm x m3/s
Flux de turbidité
FAU x m3/s.
Graphe flux-débit: résultats
Notes: If we consider the value for infiltration discharge derived from conductivity as the most reliable, we must assume that the turbidity of sanitary water is not constant
lower turbidity values during night time and higer values during day time might be a clue for sedimentation and erosion processes occuring within a daily cycle.

## Slide 18: Calage des modèles de dilution
Ajustement d’une droite pour chaque jour sec -> conductivité (variable) de l’eau usée (ou valeur par défaut si mauvais ajustement)
Ajustement global d’une conductivité des eaux d’infiltration
Ajustement global d’un profil journalier de turbidité des eaux usées
0
100
200
300
400
500
1
3
5
7
9
11
13
15
17
19
21
23
Turbidité (FAU)
Débit (m3/s)
observé
Calculé / turbidité
Notes: Here is the calibration procedure we finally applied.
Sanitary water conductivity is fitted each day, thus relaxing the overall constant conductivity assumption, but a single conductivity value is kept for infiltration.
.
For sanitary turbidity we fitted by hand a single daily pattern rather than a power function

## Slide 19: Comparaison entre les méthodes d’évaluation des débits d’infiltration et leurs paramètres
Méthode
conductivité
turbidité
Débit min.24h.
Paramètre
Turbidité moyenne
Eau usée (FAU)
Débit minimum
d’eau usée
(m
3
/s)
valeur
100
400
300
360
500
0,10
0,14
débit moyen annuel (m3/s)
0,06
0,08
0,07
0,10
0,14
0,11
0,08
Ci (S/cm)
0
0,22
Notes: And here are the results, for different values of parameters.
Infiltration discharge values are mean values over every dry day in the year, that means roughly 180
Finally we got consistent values for the scale of one year. If we compare the with the results of a popular method for assessing infiltration discharge, which relies on daily minimum flowrates, the values are consistent too. But this latter method use a somewhat arbitrary value fir sanirtary water minimum dicharge, and is very sensisitive to this paramater, so that the comparison is not really meaning ful.

## Slide 20: Evolution dans le temps des débits d’eaux claires

## Slide 21: Conclusions
Le suivi en continu de la turbidité et de la conductivité est possible et fournit des informations utiles sur le comportement du réseau amont
Le graphe flux-débit est un outil d’analyse intéressant
Le conductivité semble efficace pour évaluer les débits d’infiltration en temps sec, voire en temps de pluie
Un modèle de dilution constitue une référence pour appréhender par comparaison la dynamique spécifique des MES à partir de mesures turbidimétriques, y compris en temps sec
Le débit et la qualité des eaux usées strictes varie d’un jour à l’autre, ce qui a des répercussions sur la fiabilité des méthodes d’évaluation des débits parasites

## Slide 22
Une analyse continue
des temps secs
peut-elle intéresser
un groupe dédié
aux événements pluvieux???

## Slide 23: Graphe flux-débit
débit
Concentration infiltrations (pente)
Concentration EU (pente)
Flux.
Notes: For that purpose we used a graphical analysis tool, which is a mass discharge vs. Flow-rate chart.
Under the assumptions of the dilution model, that is a constant concentration for sanitary water and I&I and inflow, we can draw two lines, showing the mass discharge vs. Flow-rate for sanitary water and I&I

## Slide 24: Graphe flux-débit
débit
flux.
Concentration infiltrations (pente)
Infiltration
Gamme journalière
des débits EU
Concentration EU (pente)
Infiltration
Gamme journalière des flux EU
Notes: Of course both components must be added, and for a particular day, with a constant value of infiltration discharge we could get this kind of chart. The blue segments represents infiltration flow rate and discharge. The red segment is for sanitary water, with the dotted part showing the daily range of variation of sanitary water discharge and total discharge as well.

## Slide 25: Graphe flux-débit
débit
Infiltration
Flux
Notes: If infiltartion flowrate changes from one day to another, the overall discharge segment will be shifted along parrallel lines as shown here.

## Slide 26: Graphe flux-débit
débit
Infiltration
Flux
Notes: If infiltartion flowrate changes from one day to another, the overall discharge segment will be shifted along parrallel lines as shown here.

## Slide 27: Graphe flux-débit
débit
Infiltration
Flux
Notes: If infiltartion flowrate changes from one day to another, the overall discharge segment will be shifted along parrallel lines as shown here.

## Slide 28: Graphe flux-débit
débit
Flux
Concentration infiltrations (pente)
Concentration EU (pente)
Notes: And all observed values should fill a parallelogram. The gradient of one side should be equal to the concentration of sanitary water, and the gradient of the other side should equal to the concentration of infiltration water

## Slide 29: Graphe flux-débit: conductivité
débit
Flux de conductivité
(mS.m3/m.s)
Infiltration
EU
conductivité infiltrations (pente)
Conductivité EU (pente)
Notes: This should be observed for conductivity. But of course we must accept to calculate conductivity discharge with mS.m3/m.s (or if you prefer mS.m2/s) as unity, which is not a classical parametr for pollution studies

## Slide 30: Graphe flux-débit: turbidité
débit
Infiltration
Flux turbidité
(FAU.m3/s).
EU
Turbidité EU (pente)
Notes: For turbidity, the diagram should be slightly different. One side of the parrallelogram is horizontal, since the turbidity of infiltration water is expected to be near zero. The discharge is expressed as FAU.m3/s

## Slide 31
Débit (m3/s)
Conductivité de l’eau d’infiltration
(pente)
conductivité de l’eau usée
(pente)
Flux de conductivité
(mS.m3/m.s)
.
Infiltration
eau usée
Infiltration
Eau
usée
turbidité de l’eau usée
(pente)
Flux de turbidité
FAU.m3/S.
eau usée
Graphe flux-débit
Notes: For checking the assumptions and calibrating the parameters we used a graphical analysis tool, which is a mass discharge vs. Flow-rate chart.
This chart represents flow rates as ordinates, and mass-discharges as abscissae. Turbidity data are red and conductivity data are blue . So in our case the mass discharges are rather unconventional, as they rely on conductivity and turbidity rather than on real concentrations, hence some strange units like
Anyway the assumptions of the dilution model, that are constant concentrations for sanitary water and infiltration water should lead to clouds of dots with the shape of parallelograms, with the gradient of the sides respectively equal to turbidty and conductivity values of sanitary water and infiltration water. Moroever the path of data observed for different dry days should be parrallel segments.
One interesting thing is that we get two consctructions for assessing infiltration flow rate and of course they should converge on the same point.

## Slide 32: Graphe flux-débit Ecarts aux hypothèses
Cinf varie
Qinf varie
Ceu varie
Notes: This should be observed for conductivity. But of course we must accept to calculate conductivity discharge with mS.m3/m.s (or if you prefer mS.m2/s) as unity, which is not a classical parametr for pollution studies